## Size
Component | Unit | Total
Solar PV | kW | 67.91
Battery bank | kWh | 137.61
Diesel Genset 1 | kW | 13.75
Compressor | kW | 16.27

## Cost
Total
Weighted Net present cost | System | - | kUSD | 185.385
Net present cost | System | 1 | kUSD | 185.385
Total Investment cost | System | - | kUSD | 113.572
Total fixed O&M cost | System | - | kUSD | 23.537
Total variable O&M cost | System | 1 | kUSD | 48.276
Salvage value | System | - | kUSD | 0
Levelized Cost of Energy | System | - | USD/kWh | 0.2905
Levelized Cost of Energy scenarios | System | 1 | USD/kWh | 0.2905
Investment cost | Solar PV | - | kUSD | 64.514
| Battery bank | - | kUSD | 45.412
| Compressor | - | kUSD | 0.895
| Diesel Genset 1 | - | kUSD | 2.751
Fixed cost | Solar PV | - | kUSD | 6.706
| Battery bank | - | kUSD | 15.735
| Ice Tank | - | kUSD | 0.103
| Diesel Genset 1 | - | kUSD | 0.993
Lost load cost | System | 1 | kUSD | 0
Replacement cost | Battery bank | 1 | kUSD | 3.438
Fuel cost | Diesel | 1 | kUSD | 44.838
Fuel CO2 emission | System | 1 | ton | 454.775
RES CO2 emission | RES | - | ton | 0
GEN CO2 emission | GEN | - | ton | 0
BESS CO2 emission | BESS | - | ton | 0
TOTAL CO2 emission | System | 1 | ton | 454.775

## Yearly cash flows
| Fixed costs |  |  | Lost load cost | Replacement cost | Fuel cost
Component | Solar PV | Battery bank | Diesel Genset 1 | System | Battery bank | Diesel
Scenario | - | - | - | 1 | 1 | 1
Unit | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD
Year 1 | 1.16 | 2.72 | 0.17 | 0 | 0.61 | 4.36
Year 2 | 1.16 | 2.72 | 0.17 | 0 | 0.58 | 8
Year 3 | 1.16 | 2.72 | 0.17 | 0 | 0.6 | 5.43
Year 4 | 1.16 | 2.72 | 0.17 | 0 | 0.6 | 5.97
Year 5 | 1.16 | 2.72 | 0.17 | 0 | 0.6 | 6.54
Year 6 | 1.16 | 2.72 | 0.17 | 0 | 0.6 | 7.12
Year 7 | 1.16 | 2.72 | 0.17 | 0 | 0.59 | 7.75
Year 8 | 1.16 | 2.72 | 0.17 | 0 | 0.59 | 8.33
Year 9 | 1.16 | 2.72 | 0.17 | 0 | 0.59 | 8.98
Year 10 | 1.16 | 2.72 | 0.17 | 0 | 0.59 | 9.63
Year 11 | 1.16 | 2.72 | 0.17 | 0 | 0.59 | 10.31
Year 12 | 1.16 | 2.72 | 0.17 | 0 | 0.59 | 11
Year 13 | 1.16 | 2.72 | 0.17 | 0 | 0.59 | 11.72
Year 14 | 1.16 | 2.72 | 0.17 | 0 | 0.59 | 12.46
Year 15 | 1.16 | 2.72 | 0.17 | 0 | 0.59 | 13.21
Year 16 | 1.16 | 2.72 | 0.17 | 0 | 0.59 | 14.01
Year 17 | 1.16 | 2.72 | 0.17 | 0 | 0.59 | 14.83
Year 18 | 1.16 | 2.72 | 0.17 | 0 | 0.59 | 15.67
Year 19 | 1.16 | 2.72 | 0.17 | 0 | 0.59 | 16.56
Year 20 | 1.16 | 2.72 | 0.17 | 0 | 0.59 | 17.46

## Yearly energy parameters
| Generators share | Renewables penetration | Curtailment share | Battery usage | Compressor usage
| % | % | % | % | %
Year 1 | 16.6 | 92.07 | 21.78 | 54.9 | 56.65
Year 2 | 29.68 | 86.33 | 7.34 | 51.06 | 94.46
Year 3 | 19.62 | 90.3 | 20.7 | 51.62 | 53.64
Year 4 | 21.01 | 89.44 | 20.13 | 50.13 | 52.27
Year 5 | 22.42 | 88.54 | 19.58 | 48.63 | 50.92
Year 6 | 23.77 | 87.65 | 19.02 | 47.19 | 49.61
Year 7 | 25.17 | 86.71 | 18.47 | 45.77 | 48.4
Year 8 | 26.35 | 85.85 | 17.93 | 44.48 | 47.02
Year 9 | 27.68 | 84.91 | 17.36 | 43.13 | 45.88
Year 10 | 28.9 | 83.99 | 16.82 | 41.9 | 44.65
Year 11 | 30.13 | 83.05 | 16.31 | 40.7 | 43.43
Year 12 | 31.29 | 82.13 | 15.78 | 39.57 | 42.25
Year 13 | 32.48 | 81.17 | 15.23 | 38.47 | 41.17
Year 14 | 33.6 | 80.23 | 14.65 | 37.42 | 40.13
Year 15 | 34.69 | 79.28 | 14.13 | 36.41 | 39
Year 16 | 35.82 | 78.3 | 13.6 | 35.45 | 37.98
Year 17 | 36.94 | 77.31 | 13.03 | 34.5 | 37.06
Year 18 | 38 | 76.33 | 12.49 | 33.66 | 36.08
Year 19 | 39.12 | 75.31 | 11.95 | 32.94 | 35.19
Year 20 | 40.15 | 74.32 | 11.44 | 32.31 | 34.21

## Yearly energy parameters SC
| Generator share | Renewable penetration | Curtailment share | Battery usage
Component | Diesel Genset 1 | Solar PV | - | Battery bank
Scenario | 1 | 1 | 1 | 1
| % | % | % | %
Year 1 | 10.6 | 92.07 | 21.78 | 54.9
Year 2 | 15.26 | 86.33 | 7.34 | 51.06
Year 3 | 12.77 | 90.3 | 20.7 | 51.62
Year 4 | 13.8 | 89.44 | 20.13 | 50.13
Year 5 | 14.86 | 88.54 | 19.58 | 48.63
Year 6 | 15.89 | 87.65 | 19.02 | 47.19
Year 7 | 16.96 | 86.71 | 18.47 | 45.77
Year 8 | 17.93 | 85.85 | 17.93 | 44.48
Year 9 | 18.98 | 84.91 | 17.36 | 43.13
Year 10 | 19.98 | 83.99 | 16.82 | 41.9
Year 11 | 21.01 | 83.05 | 16.31 | 40.7
Year 12 | 22 | 82.13 | 15.78 | 39.57
Year 13 | 23.01 | 81.17 | 15.23 | 38.47
Year 14 | 23.98 | 80.23 | 14.65 | 37.42
Year 15 | 24.95 | 79.28 | 14.13 | 36.41
Year 16 | 25.96 | 78.3 | 13.6 | 35.45
Year 17 | 26.95 | 77.31 | 13.03 | 34.5
Year 18 | 27.93 | 76.33 | 12.49 | 33.66
Year 19 | 28.93 | 75.31 | 11.95 | 32.94
Year 20 | 29.92 | 74.32 | 11.44 | 32.31