## Size
Component | Unit | Total
Solar PV | kW | 172.82
Wind Turbine | kW | 803.13
Battery bank | kWh | 130.16
Diesel Genset 1 | kW | 17.97
Ice Tank | kg | 2122.84
Compressor | kW | 20.55

## Cost
Total
Weighted Net present cost | System | - | kUSD | 1949.289
Net present cost | System | 1 | kUSD | 1949.289
Total Investment cost | System | - | kUSD | 1738.652
Total fixed O&M cost | System | - | kUSD | 389.584
Total variable O&M cost | System | 1 | kUSD | 4.941
Salvage value | System | - | kUSD | -183.887
Levelized Cost of Energy | System | - | USD/kWh | 2.8973
Levelized Cost of Energy scenarios | System | 1 | USD/kWh | 2.8973
Investment cost | Solar PV | - | kUSD | 164.177
| Wind Turbine | - | kUSD | 1525.948
| Battery bank | - | kUSD | 42.953
| Ice Tank | - | kUSD | 0.849
| Compressor | - | kUSD | 1.13
| Diesel Genset 1 | - | kUSD | 3.594
Fixed cost | Solar PV | - | kUSD | 14.021
| Wind Turbine | - | kUSD | 362.001
| Battery bank | - | kUSD | 12.228
| Ice Tank | - | kUSD | 0.161
|  |  | kUSD | 0.107
| Diesel Genset 1 | - | kUSD | 1.066
Lost load cost | System | 1 | kUSD | 0
Replacement cost | Battery bank | 1 | kUSD | 1.048
Fuel cost | Diesel | 1 | kUSD | 3.893
Fuel CO2 emission | System | 1 | ton | 18.972
RES CO2 emission | RES | - | ton | 0
GEN CO2 emission | GEN | - | ton | 0
BESS CO2 emission | BESS | - | ton | 0
TOTAL CO2 emission | System | 1 | ton | 18.972

## Yearly cash flows
| Fixed costs |  |  |  |  | Lost load cost | Replacement cost | Fuel cost
Component | Solar PV | Wind Turbine | Battery bank | Ice Tank | Diesel Genset 1 | System | Battery bank | Diesel
Scenario | - | - | - | - | - | 1 | 1 | 1
Unit | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD
Year 1 | 2.96 | 76.3 | 2.58 | 0.03 | 0.22 | 0 | 0.2 | 0.52
Year 2 | 2.96 | 76.3 | 2.58 | 0.03 | 0.22 | 0 | 0.22 | 1.58
Year 3 | 2.96 | 76.3 | 2.58 | 0.03 | 0.22 | 0 | 0.21 | 0.57
Year 4 | 2.96 | 76.3 | 2.58 | 0.03 | 0.22 | 0 | 0.22 | 0.63
Year 5 | 2.96 | 76.3 | 2.58 | 0.03 | 0.22 | 0 | 0.22 | 0.67
Year 6 | 2.96 | 76.3 | 2.58 | 0.03 | 0.22 | 0 | 0.23 | 0.71
Year 7 | 2.96 | 76.3 | 2.58 | 0.03 | 0.22 | 0 | 0.23 | 0.8
Year 8 | 2.96 | 76.3 | 2.58 | 0.03 | 0.22 | 0 | 0.24 | 0.88
Year 9 | 2.96 | 76.3 | 2.58 | 0.03 | 0.22 | 0 | 0.25 | 0.93
Year 10 | 2.96 | 76.3 | 2.58 | 0.03 | 0.22 | 0 | 0.25 | 1

## Yearly energy parameters
| Generators share | Renewables penetration | Curtailment share | Battery usage | Ice Tank usage
| % | % | % | % | %
Year 1 | 2.09 | 99.85 | 84.5 | 16.54 | 166.9
Year 2 | 6.18 | 99.54 | 81.71 | 18.01 | 99.33
Year 3 | 2.18 | 99.83 | 84.11 | 16.53 | 167.39
Year 4 | 2.32 | 99.82 | 83.9 | 16.5 | 167.3
Year 5 | 2.42 | 99.81 | 83.69 | 16.48 | 167.28
Year 6 | 2.5 | 99.79 | 83.48 | 16.52 | 167.33
Year 7 | 2.74 | 99.77 | 83.25 | 16.49 | 166.99
Year 8 | 2.92 | 99.75 | 83.03 | 16.45 | 167.44
Year 9 | 3.01 | 99.73 | 82.8 | 16.44 | 167.27
Year 10 | 3.17 | 99.71 | 82.56 | 16.43 | 167.4

## Yearly energy parameters SC
| Generator share | Renewable penetration |  | Curtailment share | Battery usage | Ice Tank usage
Component | Diesel Genset 1 | Solar PV | Wind Turbine | - | Battery bank | Ice Tank
Scenario | 1 | 1 | 1 | 1 | 1 | 1
| % | % | % | % | % | %
Year 1 | 0.98 | 35.42 | 64.43 | 84.5 | 16.54 | 166.9
Year 2 | 2.53 | 35.31 | 64.23 | 81.71 | 18.01 | 99.33
Year 3 | 1.06 | 35.41 | 64.42 | 84.11 | 16.53 | 167.39
Year 4 | 1.14 | 35.41 | 64.41 | 83.9 | 16.5 | 167.3
Year 5 | 1.2 | 35.4 | 64.4 | 83.69 | 16.48 | 167.28
Year 6 | 1.26 | 35.4 | 64.39 | 83.48 | 16.52 | 167.33
Year 7 | 1.4 | 35.39 | 64.38 | 83.25 | 16.49 | 166.99
Year 8 | 1.51 | 35.38 | 64.36 | 83.03 | 16.45 | 167.44
Year 9 | 1.58 | 35.38 | 64.35 | 82.8 | 16.44 | 167.27
Year 10 | 1.69 | 35.37 | 64.34 | 82.56 | 16.43 | 167.4