## Size
Component | Unit | Total
Solar PV | kW | 54.19
Battery bank | kWh | 187.23
Diesel Genset 1 | kW | 19.99

## Cost
Total
Weighted Net present cost | System | - | kUSD | 131.947
Net present cost | System | 1 | kUSD | 131.947
Total Investment cost | System | - | kUSD | 87.56
Total fixed O&M cost | System | - | kUSD | 15.833
Total variable O&M cost | System | 1 | kUSD | 28.823
Salvage value | System | - | kUSD | -0.269
Levelized Cost of Energy | System | - | USD/kWh | 0.2562
Levelized Cost of Energy scenarios | System | 1 | USD/kWh | 0.2562
Investment cost | Solar PV | - | kUSD | 51.481
| Battery bank | - | kUSD | 28.084
| Diesel Genset 1 | - | kUSD | 7.995
Fixed cost | Solar PV | - | kUSD | 4.512
| Battery bank | - | kUSD | 8.205
| Diesel Genset 1 | - | kUSD | 3.115
Lost load cost | System | 1 | kUSD | 0
Replacement cost | Battery bank | 1 | kUSD | 4.795
Fuel cost | Diesel | 1 | kUSD | 24.028
Fuel CO2 emission | System | 1 | ton | 668.308
RES CO2 emission | RES | - | ton | 0
GEN CO2 emission | GEN | - | ton | 0
BESS CO2 emission | BESS | - | ton | 0
TOTAL CO2 emission | System | 1 | ton | 668.308

## Yearly cash flows
| Fixed costs |  |  | Lost load cost | Replacement cost | Fuel cost
Component | Solar PV | Battery bank | Diesel Genset 1 | System | Battery bank | Diesel
Scenario | - | - | - | 1 | 1 | 1
Unit | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD
Year 1 | 0.93 | 1.69 | 0.64 | 0 | 0.94 | 0.18
Year 2 | 0.93 | 1.69 | 0.64 | 0 | 0.99 | 0.37
Year 3 | 0.93 | 1.69 | 0.64 | 0 | 1.02 | 0.7
Year 4 | 0.93 | 1.69 | 0.64 | 0 | 1.05 | 1.29
Year 5 | 0.93 | 1.69 | 0.64 | 0 | 1.06 | 2.24
Year 6 | 0.93 | 1.69 | 0.64 | 0 | 1.05 | 3.54
Year 7 | 0.93 | 1.69 | 0.64 | 0 | 1.04 | 5.07
Year 8 | 0.93 | 1.69 | 0.64 | 0 | 1.02 | 6.72
Year 9 | 0.93 | 1.69 | 0.64 | 0 | 1 | 8.5
Year 10 | 0.93 | 1.69 | 0.64 | 0 | 0.97 | 10.43
Year 11 | 0.93 | 1.69 | 0.64 | 0 | 0.94 | 12.58
Year 12 | 0.93 | 1.69 | 0.64 | 0 | 0.91 | 14.9
Year 13 | 0.93 | 1.69 | 0.64 | 0 | 0.87 | 17.41
Year 14 | 0.93 | 1.69 | 0.64 | 0 | 0.83 | 20.09
Year 15 | 0.93 | 1.69 | 0.64 | 0 | 0.79 | 22.96
Year 16 | 0.93 | 1.69 | 0.64 | 0 | 0.75 | 26.02
Year 17 | 0.93 | 1.69 | 0.64 | 0 | 0.73 | 29.28
Year 18 | 0.93 | 1.69 | 0.64 | 0 | 0.72 | 32.74
Year 19 | 0.93 | 1.69 | 0.64 | 0 | 0.76 | 36.42
Year 20 | 0.93 | 1.69 | 0.64 | 0 | 0.83 | 40.31

## Yearly energy parameters
| Generators share | Renewables penetration | Curtailment share | Battery usage
| % | % | % | %
Year 1 | 0.58 | 99.55 | 20.84 | 53.45
Year 2 | 1.1 | 99.1 | 17.14 | 53.18
Year 3 | 1.98 | 98.33 | 13.7 | 52.57
Year 4 | 3.49 | 96.95 | 10.7 | 51.34
Year 5 | 5.77 | 94.82 | 8.37 | 49.34
Year 6 | 8.7 | 92.04 | 6.72 | 46.7
Year 7 | 11.86 | 88.98 | 5.42 | 43.84
Year 8 | 14.97 | 85.9 | 4.23 | 41.04
Year 9 | 18.03 | 82.81 | 3.17 | 38.31
Year 10 | 21.07 | 79.7 | 2.26 | 35.61
Year 11 | 24.19 | 76.51 | 1.58 | 32.86
Year 12 | 27.3 | 73.32 | 1.07 | 30.15
Year 13 | 30.37 | 70.18 | 0.69 | 27.51
Year 14 | 33.38 | 67.1 | 0.41 | 24.95
Year 15 | 36.32 | 64.09 | 0.21 | 22.56
Year 16 | 39.21 | 61.16 | 0.1 | 20.49
Year 17 | 42.02 | 58.32 | 0.03 | 18.91
Year 18 | 44.75 | 55.58 | 0.01 | 17.92
Year 19 | 47.41 | 52.94 | 0 | 17.85
Year 20 | 49.98 | 50.4 | 0 | 18.61

## Yearly energy parameters SC
| Generator share | Renewable penetration | Curtailment share | Battery usage
Component | Diesel Genset 1 | Solar PV | - | Battery bank
Scenario | 1 | 1 | 1 | 1
| % | % | % | %
Year 1 | 0.58 | 99.55 | 20.84 | 53.45
Year 2 | 1.1 | 99.1 | 17.14 | 53.18
Year 3 | 1.98 | 98.33 | 13.7 | 52.57
Year 4 | 3.49 | 96.95 | 10.7 | 51.34
Year 5 | 5.77 | 94.82 | 8.37 | 49.34
Year 6 | 8.7 | 92.04 | 6.72 | 46.7
Year 7 | 11.86 | 88.98 | 5.42 | 43.84
Year 8 | 14.97 | 85.9 | 4.23 | 41.04
Year 9 | 18.03 | 82.81 | 3.17 | 38.31
Year 10 | 21.07 | 79.7 | 2.26 | 35.61
Year 11 | 24.19 | 76.51 | 1.58 | 32.86
Year 12 | 27.3 | 73.32 | 1.07 | 30.15
Year 13 | 30.37 | 70.18 | 0.69 | 27.51
Year 14 | 33.38 | 67.1 | 0.41 | 24.95
Year 15 | 36.32 | 64.09 | 0.21 | 22.56
Year 16 | 39.21 | 61.16 | 0.1 | 20.49
Year 17 | 42.02 | 58.32 | 0.03 | 18.91
Year 18 | 44.75 | 55.58 | 0.01 | 17.92
Year 19 | 47.41 | 52.94 | 0 | 17.85
Year 20 | 49.98 | 50.4 | 0 | 18.61