## Size
Component | Unit | Total
Solar PV | kW | 65.41
Battery bank | kWh | 116.81
Diesel Genset 1 | kW | 11.2
Compressor | kW | 27.83

## Cost
Total
Weighted Net present cost | System | - | kUSD | 178.662
Net present cost | System | 1 | kUSD | 178.662
Total Investment cost | System | - | kUSD | 104.461
Total fixed O&M cost | System | - | kUSD | 20.801
Total variable O&M cost | System | 1 | kUSD | 53.4
Salvage value | System | - | kUSD | 0
Levelized Cost of Energy | System | - | USD/kWh | 0.2876
Levelized Cost of Energy scenarios | System | 1 | USD/kWh | 0.2876
Investment cost | Solar PV | - | kUSD | 62.144
| Battery bank | - | kUSD | 38.546
| Compressor | - | kUSD | 1.531
| Diesel Genset 1 | - | kUSD | 2.241
Fixed cost | Solar PV | - | kUSD | 6.46
| Battery bank | - | kUSD | 13.356
| Ice Tank | - | kUSD | 0.177
| Diesel Genset 1 | - | kUSD | 0.809
Lost load cost | System | 1 | kUSD | 0
Replacement cost | Battery bank | 1 | kUSD | 2.847
Fuel cost | Diesel | 1 | kUSD | 50.553
Fuel CO2 emission | System | 1 | ton | 510.878
RES CO2 emission | RES | - | ton | 0
GEN CO2 emission | GEN | - | ton | 0
BESS CO2 emission | BESS | - | ton | 0
TOTAL CO2 emission | System | 1 | ton | 510.878

## Yearly cash flows
| Fixed costs |  |  | Lost load cost | Replacement cost | Fuel cost
Component | Solar PV | Battery bank | Diesel Genset 1 | System | Battery bank | Diesel
Scenario | - | - | - | 1 | 1 | 1
Unit | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD
Year 1 | 1.12 | 2.31 | 0.14 | 0 | 0.5 | 5.72
Year 2 | 1.12 | 2.31 | 0.14 | 0 | 0.5 | 6.25
Year 3 | 1.12 | 2.31 | 0.14 | 0 | 0.49 | 6.78
Year 4 | 1.12 | 2.31 | 0.14 | 0 | 0.49 | 7.33
Year 5 | 1.12 | 2.31 | 0.14 | 0 | 0.49 | 7.91
Year 6 | 1.12 | 2.31 | 0.14 | 0 | 0.49 | 8.46
Year 7 | 1.12 | 2.31 | 0.14 | 0 | 0.49 | 9.09
Year 8 | 1.12 | 2.31 | 0.14 | 0 | 0.48 | 9.72
Year 9 | 1.12 | 2.31 | 0.14 | 0 | 0.48 | 10.33
Year 10 | 1.12 | 2.31 | 0.14 | 0 | 0.49 | 11.05
Year 11 | 1.12 | 2.31 | 0.14 | 0 | 0.49 | 11.73
Year 12 | 1.12 | 2.31 | 0.14 | 0 | 0.49 | 12.43
Year 13 | 1.12 | 2.31 | 0.14 | 0 | 0.49 | 13.19
Year 14 | 1.12 | 2.31 | 0.14 | 0 | 0.5 | 13.94
Year 15 | 1.12 | 2.31 | 0.14 | 0 | 0.5 | 14.78
Year 16 | 1.12 | 2.31 | 0.14 | 0 | 0.51 | 15.59
Year 17 | 1.12 | 2.31 | 0.14 | 0 | 0.51 | 16.39
Year 18 | 1.12 | 2.31 | 0.14 | 0 | 0.52 | 17.25
Year 19 | 1.12 | 2.31 | 0.14 | 0 | 0.52 | 18.17
Year 20 | 1.12 | 2.31 | 0.14 | 0 | 0.53 | 19.05

## Yearly energy parameters
| Generators share | Renewables penetration | Curtailment share | Battery usage | Compressor usage
| % | % | % | % | %
Year 1 | 21.79 | 89.49 | 21.46 | 45 | 57.12
Year 2 | 23.2 | 88.62 | 20.94 | 43.54 | 55.49
Year 3 | 24.52 | 87.77 | 20.35 | 42.22 | 54.13
Year 4 | 25.81 | 86.91 | 19.79 | 40.93 | 52.72
Year 5 | 27.11 | 86.02 | 19.26 | 39.64 | 51.35
Year 6 | 28.25 | 85.19 | 18.73 | 38.51 | 49.92
Year 7 | 29.55 | 84.26 | 18.14 | 37.35 | 48.79
Year 8 | 30.77 | 83.35 | 17.62 | 36.28 | 47.5
Year 9 | 31.83 | 82.5 | 17.08 | 35.34 | 46.17
Year 10 | 33.17 | 81.49 | 16.51 | 34.48 | 45.12
Year 11 | 34.28 | 80.58 | 16 | 33.8 | 43.83
Year 12 | 35.35 | 79.67 | 15.47 | 33.08 | 42.6
Year 13 | 36.53 | 78.69 | 14.93 | 32.45 | 41.53
Year 14 | 37.6 | 77.74 | 14.41 | 31.82 | 40.39
Year 15 | 38.81 | 76.72 | 13.88 | 31.18 | 39.45
Year 16 | 39.88 | 75.74 | 13.34 | 30.66 | 38.42
Year 17 | 40.82 | 74.81 | 12.88 | 30.13 | 37.23
Year 18 | 41.82 | 73.84 | 12.33 | 29.6 | 36.27
Year 19 | 42.91 | 72.82 | 11.82 | 29.26 | 35.36
Year 20 | 43.81 | 71.87 | 11.3 | 28.98 | 34.33

## Yearly energy parameters SC
| Generator share | Renewable penetration | Curtailment share | Battery usage
Component | Diesel Genset 1 | Solar PV | - | Battery bank
Scenario | 1 | 1 | 1 | 1
| % | % | % | %
Year 1 | 13.87 | 89.49 | 21.46 | 45
Year 2 | 14.92 | 88.62 | 20.94 | 43.54
Year 3 | 15.91 | 87.77 | 20.35 | 42.22
Year 4 | 16.9 | 86.91 | 19.79 | 40.93
Year 5 | 17.91 | 86.02 | 19.26 | 39.64
Year 6 | 18.84 | 85.19 | 18.73 | 38.51
Year 7 | 19.86 | 84.26 | 18.14 | 37.35
Year 8 | 20.86 | 83.35 | 17.62 | 36.28
Year 9 | 21.78 | 82.5 | 17.08 | 35.34
Year 10 | 22.86 | 81.49 | 16.51 | 34.48
Year 11 | 23.83 | 80.58 | 16 | 33.8
Year 12 | 24.79 | 79.67 | 15.47 | 33.08
Year 13 | 25.81 | 78.69 | 14.93 | 32.45
Year 14 | 26.78 | 77.74 | 14.41 | 31.82
Year 15 | 27.83 | 76.72 | 13.88 | 31.18
Year 16 | 28.81 | 75.74 | 13.34 | 30.66
Year 17 | 29.75 | 74.81 | 12.88 | 30.13
Year 18 | 30.69 | 73.84 | 12.33 | 29.6
Year 19 | 31.7 | 72.82 | 11.82 | 29.26
Year 20 | 32.61 | 71.87 | 11.3 | 28.98