## Size
Component | Unit | Total
Solar PV | kW | 62.39
Battery bank | kWh | 169.49
Diesel Genset 1 | kW | 12.51
Compressor | kW | 10.3

## Cost
Total
Weighted Net present cost | System | - | kUSD | 209.433
Net present cost | System | 1 | kUSD | 209.433
Total Investment cost | System | - | kUSD | 118.271
Total fixed O&M cost | System | - | kUSD | 26.509
Total variable O&M cost | System | 1 | kUSD | 64.653
Salvage value | System | - | kUSD | 0
Levelized Cost of Energy | System | - | USD/kWh | 0.3327
Levelized Cost of Energy scenarios | System | 1 | USD/kWh | 0.3327
Investment cost | Solar PV | - | kUSD | 59.272
| Battery bank | - | kUSD | 55.931
| Compressor | - | kUSD | 0.567
| Diesel Genset 1 | - | kUSD | 2.501
Fixed cost | Solar PV | - | kUSD | 6.161
| Battery bank | - | kUSD | 19.38
| Ice Tank | - | kUSD | 0.065
| Diesel Genset 1 | - | kUSD | 0.903
Lost load cost | System | 1 | kUSD | 0
Replacement cost | Battery bank | 1 | kUSD | 4.363
Fuel cost | Diesel | 1 | kUSD | 60.29
Fuel CO2 emission | System | 1 | ton | 516.596
RES CO2 emission | RES | - | ton | 0
GEN CO2 emission | GEN | - | ton | 0
BESS CO2 emission | BESS | - | ton | 0
TOTAL CO2 emission | System | 1 | ton | 516.596

## Yearly cash flows
| Fixed costs |  |  | Lost load cost | Replacement cost | Fuel cost
Component | Solar PV | Battery bank | Diesel Genset 1 | System | Battery bank | Diesel
Scenario | - | - | - | 1 | 1 | 1
Unit | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD
Year 1 | 1.07 | 3.36 | 0.16 | 0 | 0.76 | 6.53
Year 2 | 1.07 | 3.36 | 0.16 | 0 | 0.75 | 13.59
Year 3 | 1.07 | 3.36 | 0.16 | 0 | 0.76 | 7.45
Year 4 | 1.07 | 3.36 | 0.16 | 0 | 0.76 | 7.98
Year 5 | 1.07 | 3.36 | 0.16 | 0 | 0.76 | 8.61
Year 6 | 1.07 | 3.36 | 0.16 | 0 | 0.76 | 9.23
Year 7 | 1.07 | 3.36 | 0.16 | 0 | 0.76 | 9.94
Year 8 | 1.07 | 3.36 | 0.16 | 0 | 0.75 | 10.57
Year 9 | 1.07 | 3.36 | 0.16 | 0 | 0.75 | 11.29
Year 10 | 1.07 | 3.36 | 0.16 | 0 | 0.75 | 11.98
Year 11 | 1.07 | 3.36 | 0.16 | 0 | 0.75 | 12.76
Year 12 | 1.07 | 3.36 | 0.16 | 0 | 0.75 | 13.5
Year 13 | 1.07 | 3.36 | 0.16 | 0 | 0.74 | 14.31
Year 14 | 1.07 | 3.36 | 0.16 | 0 | 0.74 | 15.12
Year 15 | 1.07 | 3.36 | 0.16 | 0 | 0.74 | 15.94
Year 16 | 1.07 | 3.36 | 0.16 | 0 | 0.74 | 16.84
Year 17 | 1.07 | 3.36 | 0.16 | 0 | 0.74 | 17.75
Year 18 | 1.07 | 3.36 | 0.16 | 0 | 0.74 | 18.68
Year 19 | 1.07 | 3.36 | 0.16 | 0 | 0.75 | 19.67
Year 20 | 1.07 | 3.36 | 0.16 | 0 | 0.75 | 20.65

## Yearly energy parameters
| Generators share | Renewables penetration | Curtailment share | Battery usage
| % | % | % | %
Year 1 | 22.57 | 88.69 | 18.25 | 68.46
Year 2 | 45.68 | 79.04 | 8.41 | 66.17
Year 3 | 24.4 | 87.31 | 16.72 | 65.31
Year 4 | 25.46 | 86.52 | 16.06 | 63.59
Year 5 | 26.75 | 85.61 | 15.53 | 61.78
Year 6 | 27.92 | 84.73 | 14.97 | 59.96
Year 7 | 29.27 | 83.75 | 14.45 | 58.19
Year 8 | 30.32 | 82.9 | 13.92 | 56.54
Year 9 | 31.52 | 81.95 | 13.35 | 54.79
Year 10 | 32.59 | 81.04 | 12.83 | 53.27
Year 11 | 33.8 | 80.06 | 12.34 | 51.69
Year 12 | 34.81 | 79.15 | 11.82 | 50.26
Year 13 | 35.92 | 78.17 | 11.31 | 48.82
Year 14 | 36.96 | 77.22 | 10.76 | 47.51
Year 15 | 37.95 | 76.27 | 10.26 | 46.17
Year 16 | 39.03 | 75.27 | 9.77 | 44.93
Year 17 | 40.06 | 74.27 | 9.22 | 43.78
Year 18 | 41.05 | 73.29 | 8.71 | 42.7
Year 19 | 42.1 | 72.26 | 8.22 | 41.71
Year 20 | 43.02 | 71.28 | 7.72 | 40.85

## Yearly energy parameters SC
| Generator share | Renewable penetration | Curtailment share | Battery usage
Component | Diesel Genset 1 | Solar PV | - | Battery bank
Scenario | 1 | 1 | 1 | 1
| % | % | % | %
Year 1 | 14.62 | 88.69 | 18.25 | 68.46
Year 2 | 23.93 | 79.04 | 8.41 | 66.17
Year 3 | 16.1 | 87.31 | 16.72 | 65.31
Year 4 | 16.95 | 86.52 | 16.06 | 63.59
Year 5 | 17.96 | 85.61 | 15.53 | 61.78
Year 6 | 18.92 | 84.73 | 14.97 | 59.96
Year 7 | 19.99 | 83.75 | 14.45 | 58.19
Year 8 | 20.89 | 82.9 | 13.92 | 56.54
Year 9 | 21.88 | 81.95 | 13.35 | 54.79
Year 10 | 22.81 | 81.04 | 12.83 | 53.27
Year 11 | 23.85 | 80.06 | 12.34 | 51.69
Year 12 | 24.76 | 79.15 | 11.82 | 50.26
Year 13 | 25.75 | 78.17 | 11.31 | 48.82
Year 14 | 26.68 | 77.22 | 10.76 | 47.51
Year 15 | 27.61 | 76.27 | 10.26 | 46.17
Year 16 | 28.6 | 75.27 | 9.77 | 44.93
Year 17 | 29.55 | 74.27 | 9.22 | 43.78
Year 18 | 30.49 | 73.29 | 8.71 | 42.7
Year 19 | 31.47 | 72.26 | 8.22 | 41.71
Year 20 | 32.39 | 71.28 | 7.72 | 40.85