## Size
Component | Unit | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Total
PV panels | kW | 849 | 0 | 0 | 0 | 407 | 1256
Battery bank | kWh | 1645 | 0 | 0 | 0 | 0 | 1645
Diesel Genset | kW | 90 | 90 | 0 | 30 | 30 | 240

## Cost
Cost item | Component | Scenario | Unit | Step 1 | Step 2 | Step 3 | Step 4 | Step 5 | Total
Weighted Net present cost | System | - | kUSD | - | - | - | - | - | 2288.392
Net present cost | System | 1 | kUSD | - | - | - | - | - | 2288.392
Total Investment cost | System | - | kUSD | - | - | - | - | - | 1640.288
Total fixed O&M cost | System | - | kUSD | - | - | - | - | - | 329.062
Total variable O&M cost | System | 1 | kUSD | - | - | - | - | - | 743.174
Salvage value | System | - | kUSD | - | - | - | - | - | -424.132
Levelized Cost of Energy | System | - | USD/kWh | - | - | - | - | - | 0.2692
Levelized Cost of Energy scenarios | System | 1 | USD/kWh | - | - | - | - | - | 0.2692
Investment cost | PV panels | - | kUSD | 989.085 | 0 | 0 | 0 | 242.374 | 1231.459
| Battery bank | - | kUSD | 329 | 0 | 0 | 0 | 0 | 329
| Diesel Genset | - | kUSD | 36 | 30.44 | 0 | 7.254 | 6.134 | 79.828
| National Grid | - | kUSD | 0 | 0 | 0 | 0 | 0 | 0
Fixed cost | PV panels | - | kUSD | - | - | - | - | - | 123.226
| Battery bank | - | kUSD | - | - | - | - | - | 170.787
| Diesel Genset | - | kUSD | - | - | - | - | - | 35.049
| National Grid | - | kUSD | - | - | - | - | - | 0
Lost load cost | System | 1 | kUSD | - | - | - | - | - | 0
Replacement cost | Battery bank | 1 | kUSD | - | - | - | - | - | 77.369
Fuel cost | Diesel | 1 | kUSD | - | - | - | - | - | 665.805
Grid electricity cost | National Grid | 1 | kUSD | - | - | - | - | - | 0
Grid electricity revenue | National Grid | 1 | kUSD | - | - | - | - | - | 0
Fuel CO2 emission | System | 1 | ton | - | - | - | - | - | 2527.836
Grid CO2 emission | System | 1 | ton | - | - | - | - | - | 0
RES CO2 emission | RES | - | ton | - | - | - | - | - | 0
GEN CO2 emission | GEN | - | ton | - | - | - | - | - | 0
BESS CO2 emission | BESS | - | ton | - | - | - | - | - | 0
TOTAL CO2 emission | System | 1 | ton | - | - | - | - | - | 2527.836

## Yearly cash flows
| Fixed costs |  |  |  | Lost load cost | Replacement cost | Fuel cost | Grid cost | Grid revenue
Component | PV panels | Battery bank | Diesel Genset | Grid | System | Battery bank | Diesel | Grid | Grid
Scenario | - | - | - | - | 1 | 1 | 1 | 1 | 1
Unit | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD
Year 1 | 17.8 | 26.32 | 2.88 | 0 | 0 | 12.13 | 54.09 | 0 | 0
Year 2 | 17.8 | 26.32 | 2.88 | 0 | 0 | 12.13 | 67.51 | 0 | 0
Year 3 | 17.8 | 26.32 | 5.76 | 0 | 0 | 12.04 | 80.85 | 0 | 0
Year 4 | 17.8 | 26.32 | 5.76 | 0 | 0 | 11.95 | 93.68 | 0 | 0
Year 5 | 17.8 | 26.32 | 5.76 | 0 | 0 | 11.89 | 109.13 | 0 | 0
Year 6 | 17.8 | 26.32 | 5.76 | 0 | 0 | 11.77 | 119.94 | 0 | 0
Year 7 | 17.8 | 26.32 | 6.72 | 0 | 0 | 11.5 | 142.94 | 0 | 0
Year 8 | 17.8 | 26.32 | 6.72 | 0 | 0 | 11.31 | 154.49 | 0 | 0
Year 9 | 26.34 | 26.32 | 7.68 | 0 | 0 | 12.17 | 133.03 | 0 | 0
Year 10 | 26.34 | 26.32 | 7.68 | 0 | 0 | 12.09 | 147.92 | 0 | 0

## Yearly energy parameters
| Generators share | Renewables penetration | Curtailment share | Battery usage | Grid usage
| % | % | % | % | %
Year 1 | 13.21 | 91.38 | 24.98 | 26.72 | 0
Year 2 | 15.65 | 89.47 | 23.09 | 25.32 | 0
Year 3 | 17.63 | 87.64 | 20.57 | 23.63 | 0
Year 4 | 19.34 | 85.95 | 18.29 | 22.22 | 0
Year 5 | 21.39 | 84.01 | 16.4 | 20.99 | 0
Year 6 | 22.46 | 82.7 | 14.36 | 19.85 | 0
Year 7 | 25.47 | 80.04 | 13.51 | 18.45 | 0
Year 8 | 26.56 | 78.77 | 12.19 | 17.5 | 0
Year 9 | 22.04 | 86.44 | 32.2 | 18.15 | 0
Year 10 | 23.38 | 85.15 | 30.33 | 17.22 | 0

## Yearly energy parameters SC
| Generator share | Renewable penetration | Curtailment share | Battery usage | Grid usage
Component | Diesel Genset | PV panels | - | Battery bank | Grid
Scenario | 1 | 1 | 1 | 1 | 1
| % | % | % | % | %
Year 1 | 13.21 | 91.38 | 24.98 | 26.72 | 0
Year 2 | 15.65 | 89.47 | 23.09 | 25.32 | 0
Year 3 | 17.63 | 87.64 | 20.57 | 23.63 | 0
Year 4 | 19.34 | 85.95 | 18.29 | 22.22 | 0
Year 5 | 21.39 | 84.01 | 16.4 | 20.99 | 0
Year 6 | 22.46 | 82.7 | 14.36 | 19.85 | 0
Year 7 | 25.47 | 80.04 | 13.51 | 18.45 | 0
Year 8 | 26.56 | 78.77 | 12.19 | 17.5 | 0
Year 9 | 22.04 | 86.44 | 32.2 | 18.15 | 0
Year 10 | 23.38 | 85.15 | 30.33 | 17.22 | 0